## Sheet1
SONARtrac® TECHNICAL DATASHEET
For the Oilsands Industry
GENERAL | INSTRUMENT TAG NO. |  | TRANSMITTER | INTEGRAL/REMOTE |  | REMOTE
| SERVICE DESCRIPTION |  |  | POWER SUPPLY | VOLTAGE | 100 TO 240 VAC OR 18 TO 36 VDC
| CRITICAL INSTRUMENT |  |  |  | FREQUENCY | 50/60 Hz
| P & ID NO |  |  |  | POWER | 25 WATTS MAX, 18 WATTS TYPICAL
| PIPE | SPEC |  | ANALOG OUTPUT RANGE |  | (2) 4-20mA CHANNELS, INTERNAL OR EXTERNAL POWERED
|  | SIZE |  | OUTPUT LOAD IMPEDANCE |  | 650 OHMS MAX
|  | SCHEDULE |  | ENCLOSURE | RATING | NEMA 4X
|  | MATERIAL |  |  | MATERIAL | FIBERGLASS
PROCESS DATA | FLUID |  |  | DIGITAL OUTPUTS |  | PULSE, ALARM, HART, MODBUS ASCII/RTU RS232/485, FOUNDATION FIELDBUS H1
| FLUID STATE |  |  | PROCESSOR |  | 32-BIT DIGITAL SIGNAL PROCESSOR
| AMBIENT TEMP RANGE |  |  | DATA LOGGING CAPABILITY |  | YES
| MAX DESIGN TEMP / PRESSURE |  |  | SYSTEM DIAGNOSTICS |  | YES
| MIN DESIGN TEMP / PRESS |  |  | LOCAL DISPLAY |  | LCD WITH BACKLIGHT
| FLOW RATE | MINIMUM |  | OPERATING TEMP RANGE |  | -20°C TO +60°C (57°C ZONE 2)
|  | NORMAL |  | STORAGE TEMP RANGE |  | -30°C TO +80°C
|  | MAXIMUM |  | MOUNTING |  | PIPE OR WALL MOUNT
| PRESSURE AT NORMAL FLOW |  | ELEC | AREA ELECTRICAL CLASS |  | ORDINARY LOCATION, CLASS I DIV 2,
| PRESSURE AT MAX FLOW |  |  | APPROVAL |  | cTUVus (SAFETY),UL/DEMKO (HAZ. AREA)
| TEMP AT NORMAL FLOW |  |  | I.S. RATED |  | NO
| TEMP AT MAX FLOW |  | ACCESS | BI-DIRECTIONAL MEASURE |  | YES / PROGRAMMABLE
| LINE VELOCITY | MINIMUM |  | TOTALIZER | UNITS | GAL; LIT; M3; FT3, CUSTOM
|  | NOMINAL |  |  | DISPLAY NO OF DIGITS | 8; THEN TO EXPONENTIAL
|  | MAXIMUM |  |  | INTERNAL NO OF DIGITS | 11; THEN ROLLOVER TO 0
| FLUID CHARACTER | CLEAN/DIRTY |  | INDICATOR RANGE |  | PROGRAMMABLE
|  | STEADY/PULSE/BATCH | TRANSDUCER METER | ACTIVE / PASSIVE |  | PASSIVE
|  | CORROSIVE |  | MEASUREMENT TYPE |  | SONAR ARRAY PROCESSING
|  | WT. % SOLIDS |  | MOUNTING |  | EXTERNAL CLAMP-ON (NON-CONTACT)
|  | TYPE |  | MEASUREMENT PARAMETER |  | LIQUID, VOLUMETRIC FLOW
|  | NACE SERVICE |  | SENSOR TYPE |  | PIEZO ELECTRIC POLYMER
|  | UNUSUAL CONDITION |  | ELEMENT MATERIAL |  | PVDF
| OTHER |  |  | OPERATING TEMP RANGE |  | -40°C TO +100°C
| VISCOSITY AT NORMAL FLOW |  |  | STORAGE TEMP RANGE |  | -40°C TO +85°C
| FLOW DIRECTION (Forward or bi-directional) |  |  | ENCLOSURE | 2" - 16" | FIBERGLASS
| INSTALLATION ORIENTATION (Vertical or horizontal) |  |  |  | ABOVE 16" | STAINLESS STEEL OR FIBERGLASS
|  |  |  | RATED LINEAR RANGE |  | 1 TO 10 M/S (3 TO 30 FT/S)
|  |  |  | ACCURACY |  | ± 1% OF READING
|  |  |  | REPEATABILITY |  | ± 0.3% OF READING
| Process Water Flow Monitoring System |  |  | MIN UPSTREAM PIPE DIA (from single elbow) |  | 15 D
| CIDRA Oilsands Ltd. |  |  | MIN DOWNSTREAM PIPE DIA (from single elbow) |  | 5 D
| 1-877-CIDRA 77 |  | ELEC | AREA ELECTRICAL CLASS |  | ORDINARY LOCATION, CLASS I DIV 2, CLASS I ZONE 2
| Main Office: Wallingford, CT 203-265-0035 |  |  | APPROVAL |  | cTUVus (SAFETY),UL/DEMKO (HAZ. AREA)
| Fax: 203-294-4211 |  |  | I.S. RATED |  | NO
| Sales: Calgary, AB 403-819-1855 |  | PURCH | MANUFACTURER |  | CIDRA
| Service: FT McMurray, AB 780-792-4440 / 780-838-9836 |  |  | MODEL NUMBER |  | VF-100 or HD VF-100
|  | www.cidra.com |  | MEASUREMENT |  | CONTINUOUS LIQUID FLOW
© 2009, CiDRA, All rights reserved. BI0308 Rev. E |  |  |  |  | SONARtrac and CiDRA are registered trademarks of CiDRA